## Loading
Loading | [5 empty] | Enter your loading in the table to the left.
Name | Power (W) | Amperage (A) | Daily Use (H) | Daily Energy Cons. (WH) | Domestic Voltage (V) | 220
Lamps lamps | 30 | 0.13636 | 0.08 | 2.4 | Total Daily Consumption (WH) | 4302.4
Microwave |  | 0 | 0.17 | 0
Washing Machine | 500 | 2.2727 | 3 | 1500 | Energy Required After CC. Loss (WH) | 4780.4444
PC |  | 0 | 2 | 0 | Energy Required After Bat. Loss (WH) | 5311.6049
TV | 60 | 0.27273 | 4 | 240 | Energy Required After Inv. Loss (WH) | 5901.7833
Sound |  | 0 | 0.5 | 0 |  |  |  | inv wattage
Laptop | 40 | 0.18182 | 6 | 240 | Min. Inverter Rating (W) | 760 |  | 1000
Freezer | 130 | 0.59091 | 12 | 1560 | Min. Inverter Draw Amperage (A) | 31.6667
Fridge |  | 0 | 24 | 0 | Min. Bank Draw Amperage (A) | 15.8333 |  | 41.6667
Hudl |  | 0 | 1 | 0 |  |  |  | 6.9444
Phone |  | 0 | 4 | 0 | Inverter Efficiency (%) | 90
Radio |  | 0 | 2 | 0 | Actual Inverter Rating (W) | 988
[5 empty] | Actual Inverter Draw Amperage (A) | 41.1667
Min. To Hr. Calc. | 10 | Mins | 0.16667 | Hours | Actual Bank Draw Amperage (A) | 20.5833
760
Inverter Wattage (W)
2000
Inverter Amperage (A)
83.3333
Note on I5: Antony Cartwright: Total amount of whatt hours consumed in a day.
Note on I7: Antony Cartwright: Compensating for charge controller inefficiency.
Note on I8: Antony Cartwright: Compensating for battery inefficiency.
Note on I9: Antony Cartwright: Compensating for inverter inefficiency. This is the recommended energy target.
Note on I11: Antony Cartwright: This is the minimum rating of inverter you should use.
Note on I12: Antony Cartwright: This is the minimum amount of amperage which your battery bank wiring should deliver.
Note on I13: Antony Cartwright: The minimum amount each bank's wiring should be able to deliver.
Note on I16: Antony Cartwright: The inverter rating you plan on using - if any.

## Panel Banks
Panel Banks |  |  |  |  | Enter your panel bank details in the table to the left.
Name | Max. Voltage(V) | Max. Amperage (A) | Max. Power (W) | Avg. Voltage (V) | 70 |  | 6512 | 1.3
Bank 1 | 70 | 10 | 700 | Total Amperage (A) | 20 |  | 8465.6 | 5 | 2
Bank 2 | 70 | 10 | 700 | Total Power (W) | 1400 |  | 1693.12 |  | 4232.8
0
|  |  | 0 | Daily Sunlight (H) | 5
0
|  |  | 0 | Daily Energy Produced (WH) | 7000 | 5901.7833
0
|  |  | 0 | Charge Cont. Efficiency (%) | 90
|  |  | 0 | Charge Cont. Amperage (A) | 58.3333 |  |  | 892 | 2
|  |  | 0 | Bank Amperage (A) | 29.1667 |  |  | 1784
0
0
NB: A bank is a collection of one or more panels wired in series. | [7 empty] | 94 | 9.6
Banks are wired together in parallel.
Note on H5: Antony Cartwright: Total amperage going to the charge controller. Determines panel cable thickness.
Note on H8: Antony Cartwright: Estimated amount of hours of appropriate irradiation. Between 2-6 on average.
Note on H10: Antony Cartwright: Daily energy produced by the array.
Note on H13: Antony Cartwright: Charge controller amperage. Energy produced, converted into the bank voltage.

## Battery Banks
Battery Banks |  |  | Enter your bank details in the table.
Name | Capacity (AH) | Total Capacity (AH) | 400
Bank 1 | 200 | Total Banks | 2
Bank 2 | 200 | Battery Efficiency (%) | 90
Bank 3 |  | Bank Voltage (V) | 24
Bank 4
Bank 5 |  | Days Storage Required | 1
|  | Energy Required (WH) | 5901.7833
|  | Energy Required (AH) | 245.9076
|  | Max. Discharge Rate (%) | 80
|  | Capacity Needed (AH) | 307.3845
NB: A bank is a collection of one or more batteries wired in series.
Banks are wired together in parallel.
Note on F4: Antony Cartwright: Your total battery capacity.
Note on F7: Antony Cartwright: Bank voltage, usually; 12v, 24v, 36v or 48v.
Note on F9: Antony Cartwright: Days of storage required in case of overuse or no sun for a day.
Note on F10: Antony Cartwright: Total storage capacity required in WH assuming 100% discharge.
Note on F11: Antony Cartwright: Total storage capacity required in AH assuming 100% discharge.
Note on F13: Antony Cartwright: Recommended 10-50%, the lower, the better. 20% is deemed the most efficient.
Note on F14: Antony Cartwright: Total capacity needed in order to meet requirements.

## Wiring Guide
Wiring Guide
| Amperage (A) | Min. Cable Thickness (mm2)
Solar Cable | 20 | 4
Charge Controller | 58.3333 | 10
Inverter | 41.1667 | 7
Battery Bank | 29.1667 | 5
NB: Estimation assumes a 2 meter length cable maximum.
Note on C5: Antony Cartwright: The amperage your solar cable must carry from the panels to the charge controller.
Note on C6: Antony Cartwright: The amperage your cable must carry from the charge controller to the battery bank box.
Note on C7: Antony Cartwright: The amperage your cable must carry from the battery bank box to the inverter.
Note on C8: Antony Cartwright: The amperage your cable must carry from each battery bank to the battery box.